## Slide 1
Designing Controls for the Process Industries
by Wayne Seames, Ph.D.

## Slide 2
CHAPTER 2
Control System Fundamentals

## Slide 3: Basic Unit Operations
Motive Force – momentum transfer:
  Fluids – gases and liquids
    Movement due to a pressure difference between upstream and downstream unit operations
    Movement due to an external force such as gravity
    Usually an external force is used to increase the pressure of the fluid at strategic points in the process
    The external force is usually provided by a pump (liquids) or compressor/blower/fan (gases)

## Slide 4: Basic Unit Operations
Motive Force – momentum transfer:
  Fluids – gases and liquids
  Solids
    Conveyors/extruders
    Gravity
    Fluidization – entrainment in a gas
    Slurry – entrainment in a liquid

## Slide 5: Basic Unit Operations
Heat transfer:
  Fluids – usually by indirect heating
    Most commonly in heat exchangers
    Steam is the most common heating fluid
    Very high temperatures usually involves the flue gas from a combustion process
    Water is the most common cooling fluid
    Very low temperatures usually involves some type of refrigerant or cryogenic process

## Slide 6: Basic Unit Operations
Heat transfer:
  Fluids – usually by indirect heating
  Solids – by either indirect or direct heating
    A hot gas passed through or over the material
  Electrical resistance is common in small-scale facilities for both fluids and solids

## Slide 7: Basic Unit Operations
Mass transfer:
  Separating a stream into multiple streams
  Changing the composition of a stream

## Slide 8: Basic Unit Operations
Mass transfer - separations:
  By phase – gas, polar liquid, non-polar liquid, solid
  By differences phase equilibria
  By differences in chemical solubility – absorption/extraction/leaching
  By differences in physical attraction - adsorption

## Slide 9: Basic Unit Operations
Mass transfer - reactions:
  By chemical reactions
    Transforming the molecular makeup of a substance
  Key parameters – stoichiometry, temperature, residence time, pressure, contaminants, competing reactions
  Most reactions are facilitated by a catalyst

## Slide 10: Independent and Dependent Process Variables
Control variables - independent:
  For fluids:
    Adjustable throttle in a pipe – control valve (CV)
    Changing the opening changes the pressure drop and flow rate of the fluid
    This is the most common independent variable in the process industries

## Slide 11: Independent and Dependent Process Variables
Control variables - independent:
  Fluids - Variations in a motive force device
    Change the amount of momentum transfer into the fluid
    Vary the electrical current provided to the motor
    Use a recycle of discharge fluid with a fixed speed motor
    Change the fraction of time the pump or compressor is in operation (start/stop, on/off, etc.)

## Slide 12: Independent and Dependent Process Variables
Control variables - independent:
  Solids - Variations in a motive force device
    Change the amount of momentum transfer used to transport the solid
    Vary the electrical current provided to the motor
    Change the fraction of time the conveyor or extruder motor is in operation

## Slide 13: Independent and Dependent Process Variables
Control variables - independent:
  Electrical Resistance Heating
    Vary the electrical current using an adjustable resistance source – rheostat
    Change the fraction of time electricity is flowing through the heating circuit – open/close contact

## Slide 14: Independent and Dependent Process Variables
Measurement variables - dependent:
  We use these to:
    Measure the effect of independent variable manipulation on the process
    Determine how to manipulate independent variables

## Slide 15: Independent and Dependent Process Variables
Measurement variables - dependent:
  The most common are:
    Flow rate (volumetric for fluids, mass for solids)
    Pressure
    Temperature
    Fluid level (or weight of a solid)
    Material properties (composition, density, etc.)
    Rotational speed

## Slide 16: Independent and Dependent Process Variables
In a single parameter control loop, one dependent variable is paired with one independent variable.
We try to select a measurement (dependent) variable that is very sensitive to changes in the control (independent) variable
This is known as regulatory control

## Slide 17: The Feedback Control Loop
Manipulate the control valve
Measure the effect
Compare the measured parameter to a setpoint
Determine the degree of manipulation of the control valve based on this comparison

## Slide 18: The Feedback Control Loop
Feedback control loops are how we control the process!
Almost everything else we will learn about process control will use the feedback control loop within its strategy

## Slide 19: How to Use Feedback Control Loops to Control a Unit Operation
Step 1: Determine the degrees of control freedom using one or more material and/or energy balance(s)
Step 2: Identify what independent variables to use – one control variable for each degree of freedom
      These should be based on the objectives of the unit operation
Step 3: Identify one measurement variable for each control variable – choose a variable that is sensitive to changes in the control variable
Step 4: Construct a feedback control loop using the CV and MV you identified

## Slide 20: How to Use Feedback Control Loops to Control a Unit Operation
Example problem 1: the liquid knockout drum

## Slide 21: Example problem 1: the liquid knockout drum Step 1
MI = MO1 + MO2 + Ma
Where:
MI is the mass of material entering through the feed nozzle
MO1 is the mass of material leaving through the top outlet nozzle
MO2 is the mass of material leaving through the bottom outlet nozzle
Ma is the accumulation (or reduction ) in material in the vessel

## Slide 22: Example problem 1: the liquid knockout drum Step 1
MI = MO1 + MO2 + Ma
Where:
MI is the mass of material entering through the feed nozzle – usually set by the upstream operation (we’ll cover exceptions later)
MO1 is the mass of material leaving through the top outlet nozzle – one degree of freedom
MO2 is the mass of material leaving through the bottom outlet nozzle – one degree of freedom
Ma is the accumulation (or reduction ) in material in the vessel – satisfied by the mass balance

## Slide 23: Example problem 1: the liquid knockout drum Step 2
2 CVs needed for the two degrees
of freedom.
What are the objectives of the unit
Operation?
Remove liquid from the gas
Avoid losing gas out the bottom
Keep the pressure within the correct range

## Slide 24: Example problem 1: the liquid knockout drum Step 2
2 CVs needed for the two degrees
of freedom:
-- put CVs on the overhead gas and
bottoms liquid streams

## Slide 25: Example problem 1: the liquid knockout drum Step 3
2 MVs needed to pair to the two
CVs
-- Measure the liquid level in
the KO drum
keep it within the correct range
and no gas will leave with the liquid
and the drum’s function to remove liquid from the gas will also be accomplished

## Slide 26: Example problem 1: the liquid knockout drum Step 3
2 MVs needed to pair to the two
CVs
-- Measure the liquid level in
the KO drum
-- Measure the pressure in the top of
the drum
Will insure that the overhead gas pressure is
sufficient for downstream operations

## Slide 27: Example problem 1: the liquid knockout drum Step 4
Match up the MVs and CVs to build
the feedback control loops
The controller is the computing
device that compares the
measurement to the
setpoint and
determines how to adjust
the CV to bring the MV
closer to its setpoint.

## Slide 28: Example problem 1: the liquid knockout drum Step 4
Match up the MVs and CVs to build
the feedback control loops
The difference between the
measurement and the setpoint is
known as the error, E.
The controller adjustment is known
as the output.

## Slide 29: Example problem 1: the liquid knockout drum Step 4
Match up the MVs and CVs to build
the feedback control loops – match them up for best stability -- minimize interactions
This is an example
of a coupled
control system

## Slide 30: Example problem 1: the liquid knockout drum Step 4
Match up the MVs and CVs to build
the feedback control loops – match them up for best stability -- minimize interactions
This is an example
of a decoupled
control system

## Slide 31: Example problem 2: A Mixing Drum
Try this one . . .
Blend in the amount
of fluid B necessary
so that the combined
fluid has a pH that
matches the desired
value. Fluid A flow is
controlled by the upstream
process.

## Slide 32: Example problem 2: A Mixing Drum
Answer. . .

## Slide 33: Example problem 3: A Process-Utility Heat Exchanger to Cool the Process Stream
Now try this one . . .
Use cooling
water to reduce
the temp
of the process
fluid to a
desired value

## Slide 34: Example problem 3: A Process-Utility Heat Exchanger to Cool the Process Stream
Answer . . .

## Slide 35: Disturbance Variables
An independent variable that is not
part of the feedback control scheme
Example: the inlet flow rate
The outlet flow rates are
not disturbance variables
even though they are not
part of the control scheme –
they are dependent variables

## Slide 36: Disturbance Variables
What are the potential
DVs for this system?

## Slide 37: Feedforward Control
Is a way to use the measurement associated with a disturbance variable to adjust the control scheme.
Also known as open loop control. Why?
  There is no direct feedback from the MV to measure how well the adjustment works
A FF control loop is almost always combined with a FB control loop rather than used by itself

## Slide 38: Feedforward Control
A FF control loop is almost always combined with a FB control loop rather than used by itself:
  The error from the FF and FB controllers are added together when the responsiveness of the two control loops are similar.
  The two controllers are nested in a cascade control scheme (will cover later in this chapter) when the FF control loop is much more responsive than the FB control loop.

## Slide 39: Feedforward Control – Configuration #1
Step 1. Identify a key disturbance variable
Step 2. Identify a good measurement variable for the disturbance variable
Step 3. Construct a feedforward control loop
Step 4. Identify which feedback control loop is most sensitive to changes in the disturbance variable.
Step 5. Add the FF and FB outputs together and use the combined output to adjust the CV

## Slide 40: Example 1
How would you construct a FF/FB control scheme to adjust for changes in the inlet flow rate into a liquid knockout drum?

## Slide 41: Example 1
Answer . . .

## Slide 42: Example 2
How would you construct a FF/FB control scheme to adjust for changes in the temperature of the inlet
cooling water?

## Slide 43: Example 2
Answer . . .

## Slide 44: Related Variables
A dependent variable that is affected by a
control variable but not used
as an MV
Example: the outlet liquid
flow rate

## Slide 45: Related Variables
There are many reasons why a variable may be related:
Due to chemical or physical properties – VLE, f(T), f(P), etc.
Due to the design of the unit operation – Pump curves, etc.

## Slide 46: Related Variables
Two ways to use the information contained in related variables to improve a control scheme are:
Ratio controls
Cascade controls – which can also be used to configure FF/FB schemes

## Slide 47: Ratio Controls
Are used when there is a correlation between the desired values of two separate MVs.
Example: I want to make the correct stoichiometric ratio for a reaction - - -
A + 2B  C
Instead of just setting the flow rate of B into a reactor, I can take the ratio of B to A and compare this ratio to the setpoint – the desired value (ideally 0.5) and used by the controller.
This ratio is known as the measurement ratio.

## Slide 48: Ratio Controls
Example: I want to make the correct stoichiometric ratio for a reaction - - -
A + 2B  C
Instead of just setting the flow rate of B into a reactor, I can take the ratio of A to B and compare this ratio to the setpoint – the desired value (ideally 0.5) and used by the controller.

## Slide 49: Ratio Controls
Example: How do you get the correct ratio of B to A?

## Slide 50: Ratio Controls
Answer . . .

## Slide 51: Ratio Controls
Example: How do you get the correct air to fuel ratio?

## Slide 52: Ratio Controls
Answer . . . .

## Slide 53: Cascade Control Loops
Pairs two control loops together.
  The overall governing loop is known as the Master or outer loop
  One or more additional control loops are included. These are known as Slave or inner loops. When there are more than one slave loops, they are known as Nested Slave loops.
  The Master loop output is used to adjust the setpoint of the slave loop.

## Slide 54: Cascade Control Loops
Pairs two control loops together.
  The Master loop output is used to adjust the setpoint of the slave loop.
  This adjustment is known as an external setpoint (ESP) or remote setpoint.
    When an ESP is not used, the setpoint is specified by the control (board) operator
  The Slave loop must be around an order of magnitude more responsive to changes in its MV than the Master loop.

## Slide 55: Cascade Control Loops
Are used to make a non-responsive FB control loop more responsive.
  Recall that level and analysis are the most non-responsive of the MV parameters
  The most common is using flow slave loop to improve the responsiveness of a level control master.
  The next most common is to using a slave loop to improve the responsiveness of an analyzer control master.

## Slide 56: Cascade Control Loops
Example: Make the bottoms
level control more
responsive using a cascade
control loop.

## Slide 57: Cascade Control Loops
Answer . . .

## Slide 58: Cascade Controls
Example: Instead of measuring pH, which is an indirect but responsive MV, modify the control scheme to measure composition of “A” in the combined
fluid outlet stream. Use
a cascade control
to improve the responsiveness
of this control loop.

## Slide 59: Cascade Controls
Answer . . .

## Slide 60: Cascade Control Loops
Are used to make a non-responsive FB control loop more responsive.
Used to couple a responsive FF control loop with a less responsive FB control loop.

## Slide 61: Cascade Controls
Example: Use FF/FB type cascade control scheme to minimize the possibility that a change in the overhead vapor flow rate will cause the distillate product to go off-specification for component A.

## Slide 62: Cascade Controls
Answer:
Now smooth out the reflux recycle
back to the column . . . .

## Slide 63: Cascade Controls
Answer:

## Slide 64: Cascade Controls
Example: How can you insure that the ratio you specify for the air/fuel ratio is correct? Use a cascade control scheme to accomplish this.

## Slide 65: Cascade Controls
Answer . . .
This is known as ratio control with
feedback trim.

## Slide 66: Process Alarms
All DCS controller blocks contain high and low level alarm functions
  Usually based on the measurement value
  Can also be based on the rate of change of the MV. This is known as a deviation alarm.

## Slide 67: Safety Systems
Independent of the process measurement and control functions
Are invoked only in an emergency
  Will cause upsets in the process
  Used only when these upsets are less of a problem than not invoking the action of the safety system

## Slide 68: Safety Systems
The most common include a high-high and/or low-low alarm of a critical measurement variable
When the setpoint is reached, the safety controller interferes with the normal operation of a control variable.
  The air supply on a pneumatically operated control valve can cutoff with a block valve. The valve will go to its designed “fail” position.
  AFO = air fail to open (AFO)
  AFC = air fail to close (AFC)

## Slide 69: Safety Systems
The most common include a high-high and/or low-low alarm of a critical measurement variable
When the setpoint is reached, the safety controller interferes with the normal operation of a control variable.
  A remotely operated block valve on the process line may be closed.
  A remotely operated block valve on a secondary fluid line may be opened.

## Slide 70: Safety Systems
The most common include a high-high and/or low-low alarm of a critical measurement variable
When the setpoint is reached, the safety controller interferes with the normal operation of a control variable.
  An electrical contact may be opened (or closed)
    Note: just shutting off a pump or compressor motor is not sufficient, the piping must be physically blocked closed.

## Slide 71: Safety Systems
Pressure relief valves, also known as just “relief valves, RVs” are mechanically controlled block valves.
  The valve goes 100% open when the set pressure is reached
  The valve goes 100% closed when the pressure drops below the set pressure
    There is often an offset factor that keeps the valve open below the set pressure until the pressure drops by the offset amount).

## Slide 72: Cascade Control Loops
Add LLAL and HHAL
Safety system loops to this
KO drum.

## Slide 73: Sequential Logic Control
Used for batch and semi-batch processes
A completely different paradigm compared to continuous controls
SQL is often executed in programmable logic controllers, PLCs.
  PLC is the hardware; SQL is the functions performed – we specify the SQL and then program the SQL in the PLC (anyone need to buy a vowel?).

## Slide 74: Sequential Logic Control
SQL is specified using logic flow diagrams and sequential events tables
The basic instruments and control blocks are shown on the P&IDs, just like continuous controls

## Slide 75: Sequential Logic Control
Example: Batch mixing process. Generate a sequence of steps to perform the following batch process:
The goal of this process is to add small increments of component B to a drum or tank containing a stoichiometric excess of component A, then heat and mix the two components together until all of component B has been consumed in the reaction of A+B  C.
Once all of B has been consumed, additional component B is added to the reactor and the process is repeated until all of component A has been consumed. Now that the drum/tank contains virtually all component C, the fluid is drained out of the drum/tank.

## Slide 76: Sequential Logic Control
Answer . . .

## Slide 77: Sequential Logic Control
Now develop the logic flow diagram and the sequential logic table for this problem.

## Slide 78: Sequential Logic Control
Answer . . .

## Slide 79: Sequential Logic Control
Answer . . .

## Slide 80
CHAPTER 2
Control System Fundamentals