## Data
Four Customers Connected to a 25 kVA Transformer
Time | Cust #1 | Cust #2 | Cust #3 | Cust #4 | Total | Totals
| kW | kW | kW | kW |  | Sorted Decending
17:00 | 8.81 | 4.96 | 11.04 | 1.44 | 26.25 | 26.7
17:15 | 2.12 | 3.16 | 7.04 | 1.62 | 13.94 | 26.25
17:30 | 9.48 | 7.08 | 7.68 | 2.46 | 26.7 | 23.8
17:45 | 7.16 | 5.08 | 6.08 | 0.84 | 19.16 | 20.12
18:00 | 6.04 | 3.12 | 4.32 | 1.12 | 14.6 | 19.68
18:15 | 9.88 | 6.56 | 5.12 | 2.24 | 23.8 | 19.24
18:30 | 4.68 | 6.88 | 6.56 | 1.12 | 19.24 | 19.16
18:45 | 5.12 | 3.84 | 8.48 | 2.24 | 19.68 | 18.08
19:00 | 10.44 | 4.44 | 4.12 | 1.12 | 20.12 | 16.88
19:15 | 3.72 | 8.52 | 3.68 | 0.96 | 16.88 | 16.26
19:30 | 8.72 | 4.52 | 0.32 | 2.56 | 16.12 | 16.12
19:45 | 10.84 | 2.92 | 3.04 | 1.28 | 18.08 | 15.29
20:00 | 6.96 | 2.08 | 2.72 | 1.92 | 13.68 | 14.6
20:15 | 6.62 | 1.48 | 3.24 | 1.12 | 12.46 | 13.94
20:30 | 7.04 | 2.33 | 4.16 | 1.76 | 15.29 | 13.68
20:45 | 6.69 | 1.89 | 4.96 | 2.72 | 16.26 | 12.46
21:00 | 1.88 | 1.64 | 4.32 | 2.41 | 10.25 | 10.25

## Answers
Problem 2.1
1 For each of the customers determine:
| Customer | Customer | Customer | Customer
| #1 | #2 | #3 | #4
a. Maximum 15 minute kW demand | 10.84 | 8.52 | 11.04 | 2.72
b. Average 15 minute kW demand | 6.8353 | 4.1471 | 5.1106 | 1.7018
c. Total KWH usage in the 4 hour period | 29.05 | 17.625 | 21.72 | 7.2325
d. Load factor | 0.63056 | 0.48674 | 0.46292 | 0.62565
2. For the 25kVA transformer determine:
a. Maximum 15 minute diversified demand | 26.7
b. Maximum 15 minute non-coincident demand | 33.12
c. Utilization Factor (assume unity power factor) | 1.068
d. Diversity Factor | 1.2404
e. Load Diversity | 6.42
3. Plot the "load duration curve" for the transformer